## Sheet1
F ¦ Emergency push button 1 ¦ 513ESTOP1,PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Emergency circuit ON TROUBLESHOOTING Check the status of the container. Reset the emergency relay on P.EMS front door | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Emergency push button 2 PCS room ¦ 513ESTOP2,PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Emergency circuit ON TROUBLESHOOTING Check the status of the container. Reset the emergency relay on the container door (PCS room) | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Emergency push button 3 Battery room ¦ 513ESTOP3,PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Emergency circuit ON TROUBLESHOOTING Check the status of the container. Reset the emergency relay on the container door (battery room) | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Emergency stop from Fire detection ¦ 081K3,PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Fire occurred TROUBLESHOOTING Refer to Emergency stop procedure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Insulation control device alarm PCS1 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Insulation losses occured TROUBLESHOOTING Check the status of the container. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Emergency external ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Surge suppressor trip ¦ 001F1,PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Surge suppressor intervention TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Power supply Fire detection open ¦ 013F2,PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Main circuit breaker UPS open ¦ 101F2,PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Power supply 24Vdc CommEquip open ¦ 301F1,PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Power supply 24Vdc Safety PLC board open ¦ 301F2,PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Power supply 24Vdc Fire detection circuits open ¦ 301F7,PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Surge suppressor UPS trip ¦ 101F3,PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Surge suppressor intervention TROUBLESHOOTING Check the status of the container. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault1.13 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Fire detection alarm NAC ¦ 081K2,PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN NAC released. TROUBLESHOOTING Check the status of the container. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Emergency State ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault1 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Emergency State Activated TROUBLESHOOTING Chech Emergency Alarm/Fault or reset Emergency Chain | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ PCS Sync Master-Slave Fault ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Master and slave configuration between the PCS columns is not ok. TROUBLESHOOTING Check the status of PCS. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault2.1 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault2.2 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault2.3 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault2.4 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault2.5 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault2.6 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault2.7 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault2.8 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault2.9 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault2.10 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault2.11 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault2.12 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault2.13 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault2.14 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_Fault2.15 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Fault2 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Main circuit breaker ¦ 003Q1,PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply HVAC ¦ 011F1,PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply BB1 Ventilation Aux1 open ¦ 015F1+015T1,PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply BB1 Ventilation Aux2 open ¦ 015F2+015T2,PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply BB1 Ventilation Aux3 open ¦ 015F3+015T3,PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply BB1 Ventilation Aux4 open ¦ 015F4+015T4,PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply BB2 Ventilation Aux1 open ¦ 015F1+015T1,PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply BB2 Ventilation Aux2 open ¦ 017F2+017T2,PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply BB2 Ventilation Aux3 open ¦ 017F3+017T3,PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply BB2 Ventilation Aux4 open ¦ 017F4+017T4,PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply PCS1 open ¦ 019F1,PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply PCS2 open ¦ 019F2,PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply PEMS Fan circuits open ¦ 019F3,PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply UPS PS unit1 24Vdc open ¦ 105F2+105T2,PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply UPS PS unit2 24Vdc open ¦ 105F3+105T3,PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_Alarm1.15 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm1 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply BB1 Control Aux1 open ¦ 103F1+103T1,PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply BB1 Control Aux2 open ¦ 103F2+103T2,PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply BB2 Control Aux1 open ¦ 103F3+103T3,PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply BB2 Control Aux2 open ¦ 103F4+103T4,PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply UPS PCS1 open ¦ 107F1,PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply UPS PCS2 open ¦ 107F2,PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply 24Vdc digital PLC board open ¦ 301F3,PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply 24Vdc analog PLC board open ¦ 301F4,PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply 24Vdc PLC IO internal open ¦ 301F5,PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply 24Vdc PLC IO external open ¦ 301F6,PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_Alarm2.10 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_Alarm2.11 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_Alarm2.12 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ PCS room high temperature ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Battery room high average temperature ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Battery Room Average Temperature higher than threshold for 5 minutes TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Battery room high single temperature ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm2 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Battery Room Average Temperature higher than threshold for 30 minutes TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ BMS1 Modbus TCP communication Error ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Modbus TCP/IP comm. Fault BMS1 TROUBLESHOOTING Check comm. status or connection | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ BMS2 Modbus TCP communication Error ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Modbus TCP/IP comm. Fault BMS2 TROUBLESHOOTING Check comm. status or connection | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ HVAC Modbus TCP communication Error ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Modbus TCP/IP comm. Fault HVAC TROUBLESHOOTING Check comm. status or connection | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ PCS1 CL1 CAN communication Error ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN CAN comm. fault CL1 HD1 TROUBLESHOOTING Check comm. status or connection | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ PCS1 CL2 CAN communication Error ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN CAN comm. fault CL2 HD1 TROUBLESHOOTING Check comm. status or connection | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ PCS2 CL1 CAN communication Error ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN CAN comm. fault CL1 HD2 TROUBLESHOOTING Check comm. status or connection | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ PCS2 CL2 CAN communication Error ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN CAN comm. fault CL2 HD2 TROUBLESHOOTING Check comm. status or connection | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Master Profinet Fault ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Master Profinet comm. fault with PEMS Core TROUBLESHOOTING Check comm. status or connection | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_Alarm3.8 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_Alarm3.9 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_Alarm3.10 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_Alarm3.11 ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Surge Suppressor PCS1 shot ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Surge Suppressor PCS2 shot ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Emergency State Activated TROUBLESHOOTING Chech Emergency Alarm/Fault or reset Emergency Chain | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ State Machine 1 in Alarm ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN State Machine 1 in Fault State TROUBLESHOOTING Check State Machine 1 Alarms/Faults | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ State Machine 2 in Alarm ¦ PEMS | Errors | _DiagnosticDB_wHMI_Alarm3 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN State Machine 2 in Fault State TROUBLESHOOTING Check State Machine 2 Alarms/Faults | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Battery Room door opened ¦ 531S1,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN battery room door has been opened TROUBLESHOOTING Check presence of non authorized people | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS Room door opened ¦ 531S2,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN pcs room door has been opened TROUBLESHOOTING Check presence of non authorized people | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS Room service door opened ¦ 531S3,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN pcs room service door has been opened TROUBLESHOOTING Check presence of non authorized people | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS Room pressure switch ¦ 531S4,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN pcs room pressure switch fault TROUBLESHOOTING Check inlet air filter of the PCS room | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 high temperature ¦ 561B1,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 high temperature ¦ 561B2,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 high temperature ¦ 561B3,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 high temperature ¦ 561B4,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 high temperature ¦ 563B1,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 high temperature ¦ 563B2,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 high temperature ¦ 563B3,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 high temperature ¦ 563B4,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 high temperature ¦ 565B1,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 high temperature ¦ 565B2,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 high temperature ¦ 565B3,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 high temperature ¦ 565B4,PEMS | Warnings | _DiagnosticDB_wHMI_Warning1 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 low temperature ¦ 561B1,PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 low temperature ¦ 561B2,PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 low temperature ¦ 561B3,PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 low temperature ¦ 561B4,PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 low temperature ¦ 563B1,PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 low temperature ¦ 563B2,PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 low temperature ¦ 563B3,PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 low temperature ¦ 563B4,PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 low temperature ¦ 565B1,PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 low temperature ¦ 565B2,PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 low temperature ¦ 565B3,PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 low temperature ¦ 565B4,PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning2.12 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning2.13 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning2.14 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning2.15 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning2 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ battery room sensor high temperature ¦ 567B1,PEMS | Warnings | _DiagnosticDB_wHMI_Warning3 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor high temperature ¦ 567B2,PEMS | Warnings | _DiagnosticDB_wHMI_Warning3 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the PCS Room and fan units | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ battery room sensor high humidity ¦ 567B1,PEMS | Warnings | _DiagnosticDB_wHMI_Warning3 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high humidity inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor high humidity ¦ 567B2,PEMS | Warnings | _DiagnosticDB_wHMI_Warning3 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high humidity inside the Battery Room TROUBLESHOOTING Check the status of the PCS Room and fan units | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ battery room sensor low temperature ¦ 567B1,PEMS | Warnings | _DiagnosticDB_wHMI_Warning3 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized low temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor low temperature ¦ 567B2,PEMS | Warnings | _DiagnosticDB_wHMI_Warning3 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized low temperature inside the Battery Room TROUBLESHOOTING Check the status of the PCS Room and fan units | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ battery room sensor low humidity ¦ 567B1,PEMS | Warnings | _DiagnosticDB_wHMI_Warning3 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized low humidity inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor low humidity ¦ 567B2,PEMS | Warnings | _DiagnosticDB_wHMI_Warning3 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized low humidity inside the Battery Room TROUBLESHOOTING Check the status of the PCS Room and fan units | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ battery room high average temperature ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning3 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | _DiagnosticDB_wHMI_Warning3 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Fire detection system trouble ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning3 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN fire detection system trouble or warning TROUBLESHOOTING check status of fire detection system in particular power supply,battery connection or other warning on control board | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Insulation control device warning PCS1 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning3 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Insulation losses occured TROUBLESHOOTING Check the status of the container. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning3.12 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning3 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning3.13 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning3 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning3.14 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning3 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning3.15 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning3 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 Read Error ¦ 561B1,PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the BB Room PT100 probes | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 Read Error ¦ 561B2,PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the BB Room PT100 probes | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 Read Error ¦ 561B3,PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the BB Room PT100 probes | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 Read Error ¦ 561B4,PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the BB Room PT100 probes | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 Read Error ¦ 563B1,PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the BB Room PT100 probes | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 Read Error ¦ 563B2,PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the BB Room PT100 probes | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 Read Error ¦ 563B3,PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the BB Room PT100 probes | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 Read Error ¦ 563B4,PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the BB Room PT100 probes | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 Read Error ¦ 565B1,PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the BB Room PT100 probes | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 Read Error ¦ 565B2,PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the BB Room PT100 probes | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 Read Error ¦ 565B3,PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the BB Room PT100 probes | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PT100 Read Error ¦ 565B4,PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the BB Room PT100 probes | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning4.12 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning4.13 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning4.14 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning4.15 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning4 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS1 CL1 Synch Warning ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN PCS Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the PCS in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS1 CL2 Synch Warning ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN PCS Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the PCS in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS2 CL1 Synch Warning ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN PCS Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the PCS in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS2 CL2 Synch Warning ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN PCS Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the PCS in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS Synch Warning: No Master¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN PCS Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the PCS in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS Synch Warning: More than one Master¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN PCS Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the PCS in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS Synch Warning: Slave Error¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN PCS Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the PCS in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS Synch Warning: No Sync Active¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN PCS Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the PCS in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ HVAC unit not enabled ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN HVAC unit not Enabled TROUBLESHOOTING Check the status of the HVAC, in case enable it | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Both HVAC compressor not enabled ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Both HVAC compressor Disabled TROUBLESHOOTING Check the status of the HVAC, in case enable it | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning5.10 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning5.11 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning5.12 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_Warning5.13 ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Surge Suppressor PCS1 open ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Surge Suppressor PCS2 open ¦ PEMS | Warnings | _DiagnosticDB_wHMI_Warning5 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0