## Sheet1
A ¦ QS1 switch status ¦ 8QBA1, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and of the LV cabinet. Then reclose it. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ AC surge suppressor ¦ 10FEC1, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Surge suppressor trip. Overvoltage occured. TROUBLESHOOTING Check the status of the surge suppressor and of the LV cabinet. Replace the fuse 10QBB1 if tripped. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ HH1HD container main breaker status ¦ 11QAB1, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and of line connection. Attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ HHEH container main breaker status ¦ 11QAB2, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip. (only in power island with HHEH) TROUBLESHOOTING Check the status of the circuit breaker and of line connection. Attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ UPS main supply status ¦ 13QAB2, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker, UPS and of lamp for 230 V ac presence. Attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ UPS output supply status ¦ 15QAB1, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and UPS. Attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ HH1HD container UPS main breaker status ¦ 16QAB1, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and of line connection. Attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ HHEH container UPS main breaker status ¦ 16QAB2, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip. (only in power island with HHEH) TROUBLESHOOTING Check the status of the circuit breaker and of line connection. Attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ UPS Shunt release coil supply status ¦ 17QAB2, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and of shunt release coil. Attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ UPS 24 Vdc power supply 1 status ¦ 18QAB1+18GAA1, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip, power supply anomaly TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure, check the power supply status | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ UPS 24 Vdc power supply 2 status ¦ 18QAB2+18GAA2, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip, power supply anomaly TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure, check the power supply status | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ UPS 24 Vdc redundance mode failure¦ 18GAA3, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN power supply anomaly TROUBLESHOOTING check the power supply status | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ UPS 24 Vdc PLC control supply status ¦ 20QAB1, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and of PLC. Attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ UPS 24 Vdc PLC I/O internal supply status ¦ 20QAB2, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and of PLC. Attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ UPS 24 Vdc PLC I/O external supply status ¦ 20QAB3, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and of PLC. Attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_MValarm1.15 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MValarm1 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ UPS 24 Vdc PLC I/O safety supply status ¦ 20QAB4, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip. TROUBLESHOOTING Check the status of the circuit breaker and of PLC. Attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ UPS 24 Vdc MV cabinet supply status ¦ 21QAB1, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ temperature level ¦ TRAFO, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN An increase in temp. Is usually caused by an electrical fault that causes localized heating, or by an overload of the transf. TROUBLESHOOTING Check the status alarms of DGPT2 and check the status of the thermometer. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Gas SF6 status ¦ JO1,MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Lower gas pressure. Leakage of SF6. TROUBLESHOOTING Check the status of MV circuit-breaker, it must be open. Check the status of MV switchgear. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Disconnector status ¦ JO1,MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN It follows the MV Circuit-breaker trip due to faults on the MV interconnection line or inside the Power Island. TROUBLESHOOTING Check the status of MV circuit-breaker. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Earthing switch status ¦ JO1,MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN It allows the grounding of the system to have a safely workstation. TROUBLESHOOTING Check the status of MV circuit-breaker and disconnector J01. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Control and protection supply status ¦ JO2,MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Internal faults. TROUBLESHOOTING Check the status of MV circuit-breaker. It must be open. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spring charging motor supply status ¦ JO2,MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN MV Circuit-breaker trip and the spring has been released. After it has to be recharged by supply. TROUBLESHOOTING Check the status of MV circuit-breaker. It must be charged when the MV circuit-breaker closes. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Circuit breaker status ¦ JO2,MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN MV Circuit-breaker trip. TROUBLESHOOTING Check the status of the MV circuit breaker and attempt a reclosure. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Protection relays trip ¦ JO2,MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN MV Circuit-breaker trip due to electrical faults. TROUBLESHOOTING Check the status of the MV circuit breaker and attempt a reclosure. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Protection relays failure ¦ JO2,MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Internal faults. TROUBLESHOOTING Check the status of MV circuit-breaker. It must be open. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Disconnector status ¦ JO2,MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN MV Circuit-breaker trip due to faults on the MV interconnection line or inside the Power Island. TROUBLESHOOTING Check the status of MV circuit-breaker. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Earthing switch status ¦ JO2,MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN It allows the grounding of the system to have a safely workstation. TROUBLESHOOTING Check the status of the disconnector J02. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_MValarm2.13 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_MValarm2.14 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_MValarm2.15 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MValarm2 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Disconnector status ¦ JO3,MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN MV Circuit-breaker trip due to faults on the MV interconnection line or inside the Power Island. TROUBLESHOOTING Check the status of MV circuit-breaker. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Earthing switch status ¦ JO3,MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN It allows the grounding of the system to have a safely workstation. TROUBLESHOOTING Check the status of the disconnector J03. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Q0A main breaker status ¦TRAFOaux,MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN LV Circuit-breaker trip due to faults. TROUBLESHOOTING Check the status of the LV circuit breaker and attempt a reclosure. In case of not reclousure the MV circuit-breaker must open. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_MValarm3.3 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ UPS failure ¦ UPS, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN internal faults. TROUBLESHOOTING Check the bypass function. It must be inserted. Check the status of UPS. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_MValarm3.5 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ QOA Fuse ac status ¦ TRAFOaux,MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Fuse trip TROUBLESHOOTING Check the status of fuses and auxiliary transformer. Replace fuses. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Oil pressure level 1 ¦TRAFO, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Overpressure is usually caused by a low resistance short circuit, the electric arc indirectly causes an instantaneous pressure increase. TROUBLESHOOTING Check the stattus of transformer and of MV circuit breaker. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Oil level 1 ¦TRAFO, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN The formation of gas is generally caused by an electrical fault on the active part of the transformer. TROUBLESHOOTING Check the status of the other oil warnings and alarms. Take a sample of gas from DGPT2 and analyze it. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Oil temperature level 1 ¦TRAFO, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN An increase in temp. is usually caused by an electrical fault that causes localized heating, or by an overload of the trans. TROUBLESHOOTING Check the status alarms of DGPT2 and check the status of the thermometer. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ temperature level 1 ¦ TRAFOaux, MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN An increase in temperature is usually caused by an electrical fault that causes localized heating, or by an overload of the transformer. TROUBLESHOOTING Check the status of the aux.transformer. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_MValarm3.11 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_MValarm3.12 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_MValarm3.13 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_MValarm3.14 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare wHMI_MValarm3.15 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MValarm3 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Fan supply status ¦ 12QAB1, MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Socket supply status ¦ 12QAB2, MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Heater supply status ¦ 12QAB3, MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare supply status ¦ 13QAB1, MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ UPS Spare supply status ¦ 17QAB1, MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ UPS 24 Vdc H/T sensor supply status ¦ 20QAB5, MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ UPS 24 Vdc Spare supply status ¦ 21QAB2, MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_MVwarning1.7 ¦ MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_MVwarning1.8 ¦ MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_MVwarning1.9 ¦ MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ UPS low battery ¦ UPS, MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN The UPS is discharging itself. It needs to be recharged. TROUBLESHOOTING Check the transition of status of UPS in bypass. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ UPS battery mode ¦ UPS, MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN The UPS is charging the essential loads. TROUBLESHOOTING Check the status of UPS. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_MVwarning1.12 ¦ MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare breaker status ¦ 13QAB3, MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_MVwarning1.14 ¦ MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare wHMI_MVwarning1.15 ¦ MVSKID | Warnings | _DiagnosticDB_wHMI_MVwarning1 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Emergency push button ¦ 36SJB1, MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN The emergency push button on the LV cabinet inside the MVSKID has been pushed. The emergency chain has been activated. TROUBLESHOOTING MV circuit-breaker must open. Check the status of the MVSKID. Reset the emergency relay on LV cabinet front door | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ External break-glass Emergency push button ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN The external red emergency buttons outside the HH1HD01 have been pushed. The emergency chain has been activated. TROUBLESHOOTING MV circuit-breaker must open. Check the status of the MVSKID and of container HH1HD01. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Oil temperature level 2 trip ¦TRAFO, MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN An increase in temperature is usually caused by an electrical fault that causes localized heating, or by an overload of the transformer. TROUBLESHOOTING Check the status of MV circuit-breaker and of the transformer. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_MVfault1.3 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_MVfault1.4 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_MVfault1.5 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_MVfault1.6 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_MVfault1.7 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_MVfault1.8 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_MVfault1.9 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_MVfault1.10 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_MVfault1.11 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_MVfault1.12 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_MVfault1.13 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_MVfault1.14 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare wHMI_MVfault1.15 ¦ MVSKID | Errors | _DiagnosticDB_wHMI_MVfault1 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0